## object-Information
objectName | description | objectType | additionalURL | dataKeptDays | machineIndex | serialNumber
IN001 | {"en":"Inverter","zh_tw":"Inverter","zh_cn":"Inverter","ja":"Inverter"} | default/DefaultEquipType | https://www.sembcorp.com/en/ | 731 |  | KMA-123467
IN002 | {"en":"Inverter","zh_tw":"Inverter","zh_cn":"Inverter","ja":"Inverter"} | default/DefaultEquipType | https://www.sembcorp.com/en/ | 731 |  | KMA-123467
IP001 | {"en":"AMI Meter","zh_tw":"AMI Meter","zh_cn":"AMI Meter","ja":"AMI Meter"} | default/DefaultEquipType | https://www.sembcorp.com/en/ | 731 |  | KMA-123467

## object-Parameter
objectName | parameterName | bindingGateway | bindingGatewayTag | paramType | value | dataType | description | engUnit | spanHi | spanLo | decimalPrecision | descriptor | recType | maxChangeRatePerMin | negativeMode | recRate | calcRate | formula
IN001 | COMMS_ERROR | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter RS485 Comms Error |  | 0 | 0 | 0 |  | Current | 0 |  | 0
IN001 | N_ACW | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter AC Power | kW | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_ACWH | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Total Yield | kWH | 100 | 0 | 3 |  | Cumulative | 100 | 0 | 900
IN001 | N_ACWHDA | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Day Yield | kWH | 100 | 0 | 3 |  | Cumulative | 100 | 0 | 900
IN001 | N_ALARM1 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Alarm 1 |  | 0 | 0 | 0 |  | Current | 0 |  | 0
IN001 | N_ALARM2 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Alarm 2 |  | 0 | 0 | 0 |  | Current | 0 |  | 0
IN001 | N_ALARM3 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Alarm 3 |  | 0 | 0 | 0 |  | Current | 0 |  | 0
IN001 | N_AVAIL | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Day Avaialbility |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_DCEFFC | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Conversion Effiecincy | % | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_DCW | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter DC Power | kW | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_DVSTAT | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Discrete | Device Status | [8 empty] | 0
IN001 | N_FLTCODE | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Fault Code |  | 0 | 0 | 0 |  | Current | 0 |  | 0
IN001 | N_GRDCODE | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Grid Code |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_MAKE |  |  | Constant | HUAWEI | String | Inverter Make | [8 empty] | 1
IN001 | N_MODEL_ID | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Model ID |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_NUMMPPT | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Number of MPPT Trackers |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_NUMSTR | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Number of Strings |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_PMAX | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Maximum Power | kW | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_PN | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Rated Power (Nominal) | kW | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_QMAX_C | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Maximum VAR Consumed | kVAR- | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_QMAX_D | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Maximum VAR Delivered | kVAR+ | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_RIS | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Isolation Resistance | Ohms | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_SERNM1 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Serial Number Part 1 |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_SERNM2 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Serial Number Part 2 |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_SERNM3 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Serial Number Part 3 |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_SERNM4 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Serial Number Part 4 |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_SERNM5 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Serial Number Part 5 |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_SMAX | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Maximum Apparent Power | KVA | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_SP_YIELD | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Day Specific Yield |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN001 | N_STATE1 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Discrete | Inverter Running Status |  |  |  |  | {"1":" Standby","128":" Stop due to power rationing","16":" Grid connection with derating due to internal causes of the solar inverter","2":" Grid-connected","256":" Shutdown","32":" Normal stop","4":" Grid-connected normally","512":" Spot check","64":" Stop due to faults","8":" Grid connection with derating due to power rationing"} |  |  |  | 0
IN001 | N_STATE2 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Discrete | Inverter Operating Status |  |  |  |  | {"0":"Locked,Disconnected,No Data Collected","1":"Unlocked,Disconnected,No Data Collected","2":"Locked,Connected,No Data Collected","3":"Unlocked,Connected,No Data Collected","4":"Locked,Disconnected,Data Being Collected","5":"Unlocked,Disconnected,Data Being Collected","6":"Locked,Connected,Data Being Collected","7":"Unlocked,Connected,Data Being Collected"} |  |  |  | 0
IN001 | N_TMPCAB | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | BoxTemp (deg C) | deg C | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | COMMS_ERROR | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter RS485 Comms Error |  | 0 | 0 | 0 |  | Current | 0 |  | 0
IN002 | N_ACW | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter AC Power | kW | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_ACWH | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Total Yield | kWH | 100 | 0 | 3 |  | Cumulative | 100 | 0 | 900
IN002 | N_ACWHDA | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Day Yield | kWH | 100 | 0 | 3 |  | Cumulative | 100 | 0 | 900
IN002 | N_ALARM1 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Alarm 1 |  | 0 | 0 | 0 |  | Current | 0 |  | 0
IN002 | N_ALARM2 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Alarm 2 |  | 0 | 0 | 0 |  | Current | 0 |  | 0
IN002 | N_ALARM3 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Alarm 3 |  | 0 | 0 | 0 |  | Current | 0 |  | 0
IN002 | N_AVAIL | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Day Avaialbility |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_DCEFFC | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Conversion Effiecincy | % | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_DCW | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter DC Power | kW | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_DVSTAT | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Discrete | Device Status | [8 empty] | 0
IN002 | N_FLTCODE | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Fault Code |  | 0 | 0 | 0 |  | Current | 0 |  | 0
IN002 | N_GRDCODE | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Grid Code |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_MAKE |  |  | Constant | HUAWEI | String | Inverter Make | [8 empty] | 1
IN002 | N_MODEL_ID | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Model ID |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_NUMMPPT | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Number of MPPT Trackers |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_NUMSTR | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Number of Strings |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_PMAX | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Maximum Power | kW | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_PN | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Rated Power (Nominal) | kW | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_QMAX_C | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Maximum VAR Consumed | kVAR- | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_QMAX_D | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Maximum VAR Delivered | kVAR+ | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_RIS | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Isolation Resistance | Ohms | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_SERNM1 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Serial Number Part 1 |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_SERNM2 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Serial Number Part 2 |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_SERNM3 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Serial Number Part 3 |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_SERNM4 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Serial Number Part 4 |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_SERNM5 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Serial Number Part 5 |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_SMAX | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Maximum Apparent Power | KVA | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_SP_YIELD | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Inverter Day Specific Yield |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IN002 | N_STATE1 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Discrete | Inverter Running Status |  |  |  |  | {"1":" Standby","128":" Stop due to power rationing","16":" Grid connection with derating due to internal causes of the solar inverter","2":" Grid-connected","256":" Shutdown","32":" Normal stop","4":" Grid-connected normally","512":" Spot check","64":" Stop due to faults","8":" Grid connection with derating due to power rationing"} |  |  |  | 0
IN002 | N_STATE2 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Discrete | Inverter Operating Status |  |  |  |  | {"0":"Locked,Disconnected,No Data Collected","1":"Unlocked,Disconnected,No Data Collected","2":"Locked,Connected,No Data Collected","3":"Unlocked,Connected,No Data Collected","4":"Locked,Disconnected,Data Being Collected","5":"Unlocked,Disconnected,Data Being Collected","6":"Locked,Connected,Data Being Collected","7":"Unlocked,Connected,Data Being Collected"} |  |  |  | 0
IN002 | N_TMPCAB | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | BoxTemp (deg C) | deg C | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | COMMS_ERROR | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Meter RS485 Comms Error |  | 0 | 0 | 0 |  | Current | 0 |  | 0
IP001 | M_AP | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Active Power (kW) | kW | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_FAE | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Import Active Energy (kWh) | kWh | 100 | 0 | 3 |  | Cumulative | 100 | 0 | 900
IP001 | M_KWP | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | DB Capacity | kWP | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_RAE | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Export Active Energy (kWh) | kWh | 100 | 0 | 3 |  | Cumulative | 100 | 0 | 900
IP001 | M_YIELD_D | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Day Yield | kWh | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_IA | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Line 1 Current (Amps) | Amps | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_IB | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Line 2 Current (Amps) | Amps | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_IC | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Line 3 Current (Amps) | Amps | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_HZ | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Line Frequency (Hz) | Hz | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_PF | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Power Factor |  | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_UA | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Line 1 Volage (Volts) | Volts | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_UB | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Line 2 Volage (Volts) | Volts | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_UC | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Line 3 Volage (Volts) | Volts | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_ZT | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Cabinet Temperature | Deg C | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_APA | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Line 1 Active Power (kW) | kW | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_APB | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Line 2 Active Power (kW) | kW | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_APC | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Line 3 Active Power (kW) | kW | 100 | 0 | 3 |  | Current | 100 |  | 900
IP001 | M_SERNUM1 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Meter Serial Number in ASCII |  | 100 | 0 | 0 |  | Current | 100 |  | 900
IP001 | M_SERNUM2 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Meter Serial Number in ASCII |  | 100 | 0 | 0 |  | Current | 100 |  | 900
IP001 | M_SERNUM3 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Meter Serial Number in ASCII |  | 100 | 0 | 0 |  | Current | 100 |  | 900
IP001 | M_SERNUM4 | SG-370021-01 | #MSYS_EdgeStatus | Primitive | 0 | Number | Meter Serial Number in ASCII |  | 100 | 0 | 0 |  | Current | 100 |  | 900
IP001 | M_MAKE |  |  | Constant | Mirai | String | Meter Make | [8 empty] | 1

## object-FormulaCode
objectName | parameterName | code | sourceObjectName | sourceParameterName

## object-AlarmInformation
objectName | parameterName | alarmType | description | deadbandType | deadbandValue | almDelay | almRestoreDelay | isEnable
IN001 | COMMS_ERROR | High-Low | Inverter RS485 Comms Error | percentage | 0 | 0 | 0 | 1
IN001 | N_ALARM1 | Comparison | Inverter Alarm 1 is triggered | percentage | 0 | 0 | 0 | 1
IN001 | N_ALARM2 | Comparison | Inverter Alarm 2 is triggered | percentage | 0 | 0 | 0 | 1
IN001 | N_ALARM3 | Comparison | Inverter Alarm 3 is triggered | percentage | 0 | 0 | 0 | 1
IN001 | N_DCEFFC | Comparison |  | percentage | 0 | 0 | 0 | 1
IN001 | N_FLTCODE | Comparison | Inverter Fault Code | percentage | 0 | 0 | 0 | 1
IN001 | N_GRDCODE | Comparison | Inverter Grid Code not correct | percentage | 0 | 0 | 0 | 1
IN001 | N_TMPCAB | Comparison | Inverter Temperature Too High | percentage | 0 | 0 | 0 | 1
IP001 | COMMS_ERROR | High-Low | AMI Comms Error | percentage | 0 | 0 | 0 | 1

## object-AlarmRules
objectName | parameterName | ruleName | level | range1 | symbol1 | range2 | symbol2 | comparison | category | message
IN001 | COMMS_ERROR | H | 7 | 1 | >= |  |  | value | Fault | RS485 Error
IN001 | COMMS_ERROR | HH | 7 | 2 | >= |  |  | value | Fault | RS485 Error
IN001 | COMMS_ERROR | L | 7 | -1 | < |  |  | value | Fault | RS485 Error
IN001 | COMMS_ERROR | LL | 7 | -2 | <= |  |  | value | Fault | RS485 Error
IN001 | N_ALARM1 | GT0 | 5 | 0 | > |  |  | value | Fault | Inverter Alarm 1 is triggered
IN001 | N_ALARM2 | GT0 | 5 | 0 | > |  |  | value | Fault | Inverter Alarm 2 is triggered
IN001 | N_ALARM3 | GT0 | 5 | 0 | > |  |  | value | Fault | Inverter Alarm 3 is triggered
IN001 | N_DCEFFC | LT60 | 3 | 60 | < |  |  | value | Alarm | DC Conversion Efficiency is lower than 60%
IN001 | N_FLTCODE | GT0 | 3 | 0 | > |  |  | value | Fault | Inverter Fault Code
IN001 | N_GRDCODE | GRDCode | 1 | 65 | > | 65 | < | value | Fault | Incorrect Grid Code
IN001 | N_TMPCAB | GT90 | 5 | 95 | > |  |  | value | Alarm | Inverter Temperature Too High
IP001 | COMMS_ERROR | H | 7 | 1 | >= |  |  | value | Alarm | RS485 Error
IP001 | COMMS_ERROR | HH | 7 | 2 | >= |  |  | value | Fault | RS485 Error
IP001 | COMMS_ERROR | L | 7 | -1 | < |  |  | value | Warning | RS485 Error
IP001 | COMMS_ERROR | LL | 7 | -2 | <= |  |  | value | Fault | RS485 Error